09671

KEY MORTAR SL-HP

125 mils

# PART 1  GENERAL

## 1.01	SUMMARY

### A.	Section Includes:

1.	Fluid applied seamless flooring.

2.	Joint, edge, and termination strips.

3.	Prior to installation of structural floor slab, advise [General Contractor] [Construction Manager], in writing, of all requirements of concrete substrate regarding finish, level tolerance, and curing; see inspection in Part 3.

4.	Locate all flexible joints required. See submittals below.

5.	Accessories necessary for complete installation.

### B.	Related Sections:

1.	Cast-in-Place Concrete:  Section 03300.

a.	Concrete sub-floor to be level (maximum variation not to exceed ¼ inch in 10 feet) and to have a steel troweled finish.  No curing agents or other additives which could prevent bonding should be used unless the mechanical surface preparation method completely removes the curing agent residue or sealer.

b.	Slabs on grade must have an efficient puncture resistant vapor barrier placed directly under the slab.

2.	Sealants:  Section 07920.

3.	Gypsum Drywall:  Section 09250.

4.	Adjacent floor finishes:  Division 9.

## 1.02	REFERENCE STANDARDS

The publications listed below from a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

### A.	American Society for Testing and Materials (ASTM) Publications:

C-307	Test Method for Tensile Strength of Chemical-Resistant Mortars.

C-501	Test Method for Relative Resistance to Wear Unglazed Ceramic Tile by the Taber Abraser.

C-531	Test Method for Linear Shrinkage and Coefficient of Thermal Expansion of Chemical-Resistant Mortars, Grouts, and Monolithic Surfacing.

C-579	Test Methods for Compressive Strength of Chemical-Resistant Mortars and Monolithic Surfaces.

C-580	Test Method for Flexural Strength and Modulus of Elasticity of Chemical-Resistant Mortars, Grouts, and Monolithic Surfacing.

C-884	Test Method for Thermal Compatibility Between Concrete and an Epoxy Resin Overlay.

D-570	Water Absorption of Plastics.

D-695	Compression Properties of Rigid Plastic.

### B.	Military Specifications (Mil. Spec.)

MIL D-3 134 F	(Impact Resistance)  Section 4.7.3.

MIL D-3 134 F	(Indentation Resistance)  Section 4.7.4.

MIL D-3234  F	(Resistance to Elevated Temperature) Section 4.7.5.

### C.	ACI 301 Specifications for Structural Concrete for Buildings (most recent edition).  Committee in Concrete 403 bulletin 59-43, Bond Strength to Concrete.

## 1.03	DEFINITIONS

A.	Epoxy Resin Flooring specified under this section is referenced on the drawings as [____].

## 1.04	SYSTEM DESCRIPTION

A.	System shall be 1/8 inch epoxy surfacing with chemical resistant epoxy sealer.

## 1.05	SUBMITTALS

A.	Samples:  Submit 6 by 6 inch cured samples of flooring system indicating color combination and non-skid properties.  Approved samples will be used during installation for product match.

B.	Certified Test:  Submit two copies of suppliers/ manufacturers written certification that flooring system meets or exceeds required properties.

C.	Manufacturers Application Instructions:  Submit descriptive data and specific recommendations for mixing, application, curing including any precautions of special handling instructions required to comply with the Occupational Safety and Health Act.

D.	Shop Drawings:  Shop Drawings shall be furnished showing installation of cove base and termination details, and details at floor material transitions and where adjoining equipment.

1.	Locate and provide detailing for flexible joints required for flooring in area of installation.

E.	Maintenance Instructions:  Submit current copies of the flooring manufacturer's printed recommendations on maintenance methods and products.  Submit in accordance with Section 01730 - Operation and Maintenance Manuals.

## 1.06	QUALITY ASSURANCE

A.	Materials used in the floor surfacing shall be the products of a single manufacturer.

B.	Installation shall be performed by an applicator with minimum 3 years experience in work of similar nature and scope.  Installer must be approved by the manufacturer of the floor surfacing materials.  The contractor shall furnish a written statement from the manufacturer that the installer is acceptable.

C.	Installer to verify locations of all flexible joints required by the provisions of this Section and by the recommendations of the related material manufacturers.

1.	Joint locations may or may not be shown in drawings.

2.	Refer to drawings required under submittals above.

D.	Installer to keep daily log of the date of installation, room number, type, color, and method of application of product being installed.  Log must be available for inspection by the Architect upon request.

E.	Contractor to have proven experience with specified system.

F.	Portable mock-up:  Prior to starting application of flooring, provide full scale portable mock-up to establish acceptable quality, durability, and appearance.  Mock-up size must not be less than 4 square feet.

1.	Acceptable mock-up to be standard of quality for installed work.

2.	Unacceptable installed work to be removed and replaced until acceptable. Aesthetically unacceptable but well bonded work may be overlaid or recoated per Manufacturer’s instructions if thickness clearances permit.

G.	Qualifications:

1.	Installer:  Must be acceptable to Architect, and Manufacturer.

## 1.07	PROJECT CONDITIONS

A.	Maintain the ambient room and the floor temperatures at 60 degrees Fahrenheit, or above, for a period extending from 72 hours before, during and after floor installation.  Concrete to receive surfacing shall have cured for at least 28 days and shall have been free of water for at least 7 days.

B.	Dew Point: Substrate temperature must be minimum of 5 degrees above dew point prior to, during or up to 24 hours after application of flooring system.

C.	Illumination: Apply flooring system only where a minimum of 30 footcandles exist when measured 3 feet from surface.

D.	Advise other trades of fixtures and fittings not to be installed until flooring is cured and protected.

## 1.08	PROTECTION

A.	Protect adjacent surfaces not scheduled to receive the flooring by masking, or by other means, to maintain these surfaces free of the flooring material.

B.	Provide adequate ventilation and fire protection at all mixing and placing operations.  Prohibit smoking or use of spark or flame producing devices within 50 feet of any mixing or placing operation.

C.	Provide polyethylene or rubber gloves or protective creams for all workmen engaged in applying products containing epoxy.

## 1.09	PRODUCT DELIVERY, STORAGE, AND HANDLING

A.	All materials shall be delivered to project site in original manufacturer's sealed containers including type of material, batch numbers, date of manufacture, and pertinent labels intact and legible.

B.	Store materials in dry protected area at a temperature between 60° F to 80° F.

C.	Follow all manufacturer's specific instructions and prudent safety practices for storage and handling.

## 1.10	WARRANTY

A.	Contractor to guarantee work under this Section to be free from defects of material and installation for the duration of the warranty period.  Defects occurring during warranty period shall be repaired, in a manner satisfactory to the Owner and the  Architect, at no additional cost to the Owner.

1.	Warranty Period:  One (1) Year.

# PART 2  PRODUCTS

## 2.01	MANUFACTURERS

A.	Specifications and quality of design standard (basis of design) based on Key Resin Company: Key Mortar SL-HP.

Key Resin Company: 888-943-4532, www.keyresin.com

B.	System description: Heavy duty, three-component epoxy resin surfacing sealed with Key #625 chemical resistant epoxy.

C.	Alternative manufacturers must have as a minimum the standards set forth in this specification and must be preapproved in accordance with project requirements.

## 2.02	MATERIALS

A.	Cementitious Tile Backboard:  See Section 09250 - Gypsum Drywall.

B.	Flexible Membrane:  Flexible Epoxy.

C.	Prime Coat:  Two component penetrating damp-proof epoxy.

D.	Matrix:  Matrix-epoxy/aggregate composition.

E.	Sealer: Two component bis-F epoxy.

## 2.04	MIXING

A.	Apply resinous flooring to specified physical properties.

B.	Provide finish that matches approved sample.  Sample to be approved by Owner and Architect.

## 2.05	FINISHES

A.	Color as selected by Architect or Owner from the manufacturer's standard colors.

# PART 3  EXECUTION

## 3.01	PREPARATION

A.	Obtain Architect's approval of mock-up before installing flooring; see QUALITY ASSURANCE in PART 1.

B.	Preparation of Surface:

1.	Inspect surfaces to receive flooring and verify that condition is smooth and free from conditions that will adversely affect execution, permanence, or quality of work.

a.	Remove all projections, all debris detrimental to flooring system, and dirt, oil contaminates, grease, and surface coatings affecting bond.

2.	Notify Architect or Owner in writing prior to commencing work of any conditions deemed unsatisfactory for the installation; installation of flooring materials is understood as acceptance of the substrate as satisfactory.

3.	Concrete:  The General Contractor shall be responsible for hiring an independent testing service to test for moisture content and moisture vapor emission rate; install no flooring over concrete until the concrete has been cured and is sufficiently dry to achieve permanence with flooring as determined by material manufacturer's recommended bond and moisture tests.

a.	Effectively remove concrete laitance by steel shot blasting or other method approved by flooring manufacturer.

b.	Concrete slab shall have an efficient puncture-resistant moisture vapor barrier 10 mils thick minimum placed directly under the concrete slab (for slab on grade).  Testing must be done to verify that the moisture vapor emission rate of the slab does not exceed that as recommended by the manufacturer at time of installation of the flooring or at any future date.  Moisture vapor emission and moisture content testing must conform with the requirements of ASTM F-1869-98 (Calcium Chloride Test) and ASTM F-2170-02 (Relative Humidity Probe Test).  If test results show excessive levels of moisture content or vapor emission rate, installation shall not proceed until source of excessive moisture is identified and removed or corrected.  If excessive moisture cannot be removed or prevented, apply manufacturer’s recommended moisture vapor emission control material.

c.	Treat cracks in concrete using manufacturer's recommended practice.  Rout out crack and fill with rigid epoxy; Reinforce crack with fiberglass cloth.  Refer to section 3.02.B.

## 3.02	INSTALLATION

A.	Install all floor materials in strict conformance with manufacturer's instructions.

B.	Route out all cracks (larger than 1/32” width) and fill with Key Crack Filler or other material approved by Manufacturer of floor materials.  Reinforce crack with fiberglass cloth using Key #502 Primer or the epoxy used to fill the crack.

C.	Prime entire surface with recommended primer.

D.	Apply epoxy surfacing to achieve a minimum thickness of 1/8 inch.  Allow to cure.

E.	Apply Key #625 chemical resistant epoxy at coverage rate of 100-125 square feet per gallon.  Allow to cure.  Apply second coat of Key #625 chemical resistant epoxy at coverage rate of 125-150 square feet per gallon.  Allow to cure.

F.	Match finished work to approved samples, uniform in thickness, sheen, color, pattern and texture, and free from defects detrimental to appearance.

G.	Apply temporary protection until floor is fully cured.  The General Contractor shall protect the finished floor from the time that the sub-contractor completes the work.

## END OF SECTION